## Settings_ReadMe
The references used in this workbook refer to the references on the mark up saved here:
(insert hyperlink here)
Quick Explanation:
On the "Pipe Section" worksheet, the user inputs the number of outlets for each section (under "additional outlets this section") and the sections which are fed from that section (under "feeds section")
The running total of outlets served by each section is then calculated and the corresponding HWS, CWS, MWS and RWS demand units and pipe sizes are determined
The method used to determine the flowrates and pipe diameters was copied from Chris's CWS workbook
Only cells with a yellow background should be filled in by the user
The demand units used in this workbook are set below
Demand Unit (Plumbing Guide)
Outlet | Hot | Cold | Main | Rain
WHB | 2 | 2
WC (CWS) |  | 2
WC (RWS) |  |  |  | 2
Bath | 10 | 10
Shower | 6 | 6
Sink (Cold) | 5 | 5
Sink (Main) | 5 | 5 | 5
Hot Tap | 5
Cold Tap |  | 5
Main Tap |  |  | 5
Rain Tap |  |  |  | 5
If you can't follow what's going on ask Richard Seaman.
Record of Changes:
2016-05-24 | Added MWS and RWS and split demand units for each type. Also added more outlets

## Pipe Section
[11 empty] | Additional Outlets this section | [10 empty] | All outlets fed through this section | [10 empty] | HWS |  |  | CWS |  |  | MWS |  |  | RWS
Section Ref | HWS | CWS | MWS | RWS | Feeds Sections (leave blank if none) |  |  |  |  | Section Description | WHB | WC (CWS) | WC (RWS) | Bath | Shower | Sink (CWS) | Sink (MWS) | Tap (HWS) | Tap (CWS) | Tap (MWS) | Tap (RWS) | WHB | WC (CWS) | WC (RWS) | Bath | Shower | Sink (CWS) | Sink (MWS) | Tap (HWS) | Tap (CWS) | Tap (MWS) | Tap (RWS) | Total DU | Flowrate | Dia | Total DU | Flowrate | Dia | Total DU | Flowrate | Dia | Total DU | Flowrate | Dia
# | mm | mm | mm | mm | # | # | # | # | # |  | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | [11 empty] | DU | kg/s | mm | DU | kg/s | mm | DU | kg/s | mm | DU | kg/s | mm |  |  | formula to determine this coulumn's letter:
1 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  |  |  | AX
2 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
3 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | Stolen from Chris's Workbook: (used to workout flowrates from demand units
4 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | From plumbing Engineering Services Design Guide Graph 3: Pipe Sizing chart - copper and stainless steel
5 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | DU | Flowrate
6 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
7 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 3 | 0.15
8 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 5 | 0.2
9 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 10 | 0.3
10 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 20 | 0.42
11 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 30 | 0.55
12 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 40 | 0.7
13 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 50 | 0.8
14 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 70 | 1
15 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 100 | 1.25
16 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 200 | 2.2
17 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 400 | 3.5
18 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 800 | 6
19 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 1000 | 7
20 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 1500 | 9
21 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 2000 | 15
22 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 5000 | 20
23 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 8000 | 30
24 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
25 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0

## INFO
Calculations Information Sheet
Note: Do not change the name of this sheets tab
Checked
The following project information is filled out when the calculation is first created: |  | Date | Engineer
Project Name
Project Number
Date Of Calc Creation
Engineer for First use
Index File Location | j:\DN07219\calculations\
Record Of Edits
Date | Engineer / Comments